Copyright 2018 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek Inc. for the AIA

SECTION 104416 - FIRE EXTINGUISHERS

First Edition: 06-01-2021

(Consultant shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”)

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes the requirements for the following types of fire extinguishers:

- <edit for project>

          - Portable, hand-carried fire extinguishers.

          - Wheeled fire extinguishers.

        - Related Requirements:

          - Section 104413 "Fire Protection Cabinets."

          - Section 233813 "Commercial-Kitchen Hoods" for fire-extinguishing systems provided as part of commercial-kitchen exhaust hoods. <delete if not required>

      - ACTION SUBMITTALS

        - Product Data: For each type of product. Include rating and classification, material descriptions, dimensions of individual components and profiles, and finishes for fire extinguishers.

        - Product Schedule: For fire extinguishers. Coordinate final fire-extinguisher schedule with fire-protection cabinet schedule to ensure proper fit and function. Indicate extinguisher type and location. <Use same designations indicated on Drawings>

      - INFORMATIONAL SUBMITTALS

        - Warranty: Sample of special warranty.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: For fire extinguishers to include in maintenance manuals.

      - COORDINATION

Consider retaining this article if fire-protection cabinets are specified by series only or for complex projects.

        - Coordinate type and capacity of fire extinguishers with fire-protection cabinets to ensure fit and function.

      - WARRANTY

        - Special Warranty: Manufacturer's standard form in which manufacturer agrees to repair or replace fire extinguishers that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Failure of hydrostatic test according to NFPA 10 when testing interval required by NFPA 10 is within the warranty period.

            - Faulty operation of valves or release levers.

          - Warranty Period: Six (6) years from date of Substantial Completion.

- PRODUCTS

      - PERFORMANCE REQUIREMENTS

        - NFPA Compliance: Fabricate and label fire extinguishers to comply with NFPA 10, "Portable Fire Extinguishers."

        - Fire Extinguishers: Listed and labeled for type, rating, and classification by an independent testing agency acceptable to authorities having jurisdiction.

      - PORTABLE, HAND-CARRIED FIRE EXTINGUISHERS <Edit for Project>

        - Fire Extinguishers: Type, size, and capacity for each type of extinguisher indicated below:

          - Multipurpose Dry-Chemical Type: Kidde Model FX340SC-2, 3A:40B:C, 5 lb.

          - Carbon Dioxide Type: Amerex Model 322, 5B:C, 5 lb.

          - Carbon Dioxide Type, MR Conditional: Badger Model B5V-2 MR, 5B:C, 5 lb.

          - Carbon Dioxide, High-Voltage Rooms: Buckeye Model 46100, 10B:C, 15 lb.

          - Clean-Agent Type, MR Conditional: Ansul Model FE13NM, 1A:10B:C 20 lb.

        - Accessories: Provide the following accessories as indicated on the drawings and details:

          - Mounting bracket for exposed wall fire extinguishers

          - Fire extinguisher cabinet for concealed installation.

      - WHEELED FIRE EXTINGUISHERS

- <Insert drawing designation or delete if not required>

        - Wheeled Fire Extinguishers: Type, size, and capacity for locations indicated, complete with carriage.

          - Dry-Chemical Type: Amerex Model B570, Class D 30 lb.

Insert other types and capacities to suit Project.

- EXECUTION

      - EXAMINATION

        - Examine fire extinguishers for proper charging and tagging.

          - Remove and replace damaged, defective, or undercharged fire extinguishers.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

        - General: Install fire extinguishers in locations indicated and in compliance with requirements of authorities having jurisdiction.

          - All extinguishers installed in finished spaces (labs, offices, corridors, lobbies, etc.) shall be installed in cabinets in accordance with Section 104413 "Fire Protection Cabinets."

          - All extinguishers installed in unfinished spaces (mechanical rooms, switchgear rooms, etc.). shall be wall-mounted with manufacturer’s bracket.

            - Mounting Brackets: Top of fire extinguisher shall be at 42 inches above finished floor.

            - Mounting Brackets: Fasten mounting brackets to surfaces, square and plumb, at locations indicated.

END OF SECTION 104416