SECTION 220516 – EXPANSION FITTINGS AND LOOPS FOR PLUMBING PIPING

First Edition 5-16-2017

(Engineer shall edit specifications and blue text in header to meet project requirements. This includes but is not limited to updating Equipment and/or Material Model Numbers indicated in the specifications and adding any additional specifications that may be required by the project. Also turn off all “Underlines”.)

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this section and all other sections of Division 22.

      - SUMMARY

        - This section includes the requirements for expansion fittings, and loops using the following:

          - Metal-bellows packless expansion joints.

          - Rubber packless expansion joints.

          - Alignment guides and anchors.

      - PERFORMANCE REQUIREMENTS

        - Compatibility: Products shall be suitable for piping service fluids, materials, working pressures, and temperatures.

        - Capability:  Products to absorb 200% of maximum axial movement between anchors.

      - ACTION SUBMITTALS

        - Product Data:  For each product specified, include manufacturers cut sheets, dimensional data, performance data, installation instructions, specified options, and warranty information.

        - Delegated-Design Submittal: For each anchor and alignment guide indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation. < Delete paragraph ‘B’ if not required>

          - Design Calculations: Calculate requirements for thermal expansion of piping systems and for selecting and designing expansion joints, loops, and swing connections.

          - Anchor Details: Detail fabrication of each anchor indicated. Show dimensions and methods of assembly and attachment to building structure.

          - Alignment Guide Details: Detail field assembly and attachment to building structure.

          - Schedule: Indicate type, manufacturer's number, size, material, pressure rating, end connections, and location for each expansion joint.

      - INFORMATIONAL SUBMITTALS

        - Welding certificates.

        - Product Certificates:  For each type of expansion joint, from manufacturer.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data: Include a copy of the approved submittal for each product and material along with applicable maintenance data in the project operation and maintenance manual.

      - QUALITY ASSURANCE

        - Welding Qualifications:  Qualify procedures and personnel according to the following:

          - AWS D1.1/D1.1M, "Structural Welding Code - Steel."

          - ASME Boiler and Pressure Vessel Code:  Section IX.

      - WARRANTY/GUARENTEE

        - See Division 22, Specification Section “Basic Mechanical Requirements – Plumbing” for warranty and guarantee requirements.

- PRODUCTS

      - GENERAL PRODUCT REQUIREMENTS

        - Equipment Design and Selection: Expansion fittings, anchors, guides and loops shall be designed and selected, for the intended use, in accordance with the scheduled capacities on the drawings and the requirements of this specification.

        - Acceptable Manufacturers: Subject to compliance with requirements, provide expansion fittings, joints, and guides by one (1) of the following:

          - Expansion Joints :

            - Adsco Manufacturing LLC.

            - Metraflex Inc.

            - Tozen Corp.

            - Vibration Mountings.

          - Alignment Guides:

            - Advanced Thermal Systems Inc.

            - Grinnell Corp.

            - Metraflex Inc.

      - PACKLESS EXPANSION JOINTS

        - Metal-Bellows Packless Expansion Joints:<Select type expansion joint for project>

          - Standards: ASTM F 1120 and EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

          - Type:  Circular, corrugated bellows with external tie rods.

          - Minimum Pressure Rating:  175 psig.

          - Expansion Joints for Copper Tubing: Two (2) ply phosphor-bronze bellows, copper pipe ends, and brass shrouds.

            - End Connections for Copper Tubing two (2) and Smaller:  Solder joint or threaded.

            - End Connections for Copper Tubing two and one half (2-1/2) to four (4) inches:  Solder joint or threaded.

            - End Connections for Copper Tubing five (5) inches and Larger:  Flanged.

        - Rubber Packless Expansion Joints:

          - Standards: ASTM F 1123 and FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

          - Material:  Fabric-reinforced rubber complying with FSA-NMEJ-703.

          - Spherical Type:  Single or double spheres with external control rods.

          - Minimum Pressure Rating: 175 psig at 240°F.

          - Material for Water:  butyl rubber.

          - End Connections: Full-faced, integral steel flanges with steel retaining rings drilled to match flange bolt holes over entire surface of flanges.

        - Expansion Compensator expansion Joint:

          - Standards: ASTM F 1123 and FSA's "Technical Handbook: Non-Metallic Expansion Joints and Flexible Pipe Connectors."

          - Type:  Two (2) ply phosphor bronze bellows, brass shrouds, and end fittings for copper piping systems and two (2) ply stainless-steel bellows, carbon-steel shrouds, and end fittings for steel piping systems. Include internal guides, antitorque device, and removable end clip for proper positioning.

          - Minimum pressure rating: for 60 psig minimum for pressure systems and for 175 psig minimum for high-pressure systems.

      - ALIGNMENT GUIDES AND ANCHORS

        - Alignment Guides:

          - Description: Steel, factory-fabricated alignment guide, with bolted two (2) section outer cylinder and base for attaching to structure; with two (2) section guiding spider for bolting to pipe.

        - Anchor Materials:

          - Steel Shapes and Plates:  ASTM A 36/A 36M.

          - Bolts and Nuts:  ASME B18.10 or ASTM A 183, steel hex head.

          - Washers:  ASTM F 844, steel, plain, flat washers.

          - Mechanical Fasteners:  Insert-wedge-type stud with expansion plug anchor for use in hardened portland cement concrete, with tension and shear capacities appropriate for application.

            - Stud:  Threaded, zinc-coated carbon steel.

            - Expansion Plug:  Zinc-coated steel.

            - Washer and Nut:  Zinc-coated steel.

          - Chemical Fasteners: Insert-type-stud, bonding-system anchor for use with hardened portland cement concrete, with tension and shear capacities appropriate for application.

            - Bonding Material: ASTM C 881/C 881M, Type IV, Grade 3, two (2) component epoxy resin suitable for surface temperature of hardened concrete where fastener is to be installed.

            - Stud: ASTM A 307, zinc-coated carbon steel with continuous thread on stud unless otherwise indicated.

            - Washer and Nut:  Zinc-coated steel.

- EXECUTION

      - EXPANSION-JOINT INSTALLATION <Designer shall locate expansion compensators and loops or drawings>

        - Install expansion joints of sizes matching sizes of piping in which they are installed.

        - Install metal-bellows expansion joints according to EJMA's "Standards of the Expansion Joint Manufacturers Association, Inc."

        - Install rubber packless expansion joints according to FSA-NMEJ-702.

      - PIPE LOOP AND SWING CONNECTION INSTALLATION

        - Install pipe loops cold-sprung in tension or compression as required to partly absorb tension or compression produced during anticipated change in temperature.

        - Connect risers and branch connections to mains with at least five (5) pipe fittings including tee in main.

        - Connect risers and branch connections to terminal units with at least four (4) pipe fittings including tee in riser.

        - Connect mains and branch connections to terminal units with at least four (4) pipe fittings including tee in main.

      - ALIGNMENT GUIDE AND ANCHOR INSTALLATION<Designer shall locate pipe anchors on drawings>

        - Install alignment guides to guide expansion and to avoid end-loading and torsional stress.

        - Install guide(s) on each side of pipe expansion fittings and loops.  Install guides nearest to expansion joint not more than pipe diameters from expansion joint.

        - Attach guides to pipe and secure guides to building structure.

        - Install anchors at locations to prevent stresses from exceeding those permitted by ASME B31.9 and to prevent transfer of loading and stresses to connected equipment.

        - Anchor Attachments:

          - Anchor Attachment to Black-Steel Pipe:  Attach by welding.  Comply with ASME B31.9 and ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

          - Anchor Attachment to Galvanized-Steel Pipe:  Attach with pipe hangers.  Use MSS SP-69, Type 42, riser clamp welded to anchor.

          - Anchor Attachment to Copper Tubing:  Attach with pipe hangers.  Use MSS SP-69, Type 24, U-bolts bolted to anchor.

        - Fabricate and install steel anchors by welding steel shapes, plates, and bars.  Comply with ASME B31.9 and AWS D1.1/D1.1M.

          - Anchor Attachment to Steel Structural Members:  Attach by welding.

          - Anchor Attachment to Concrete Structural Members:  Attach by fasteners.  Follow fastener manufacturer's written instructions.

        - Use grout to form flat bearing surfaces for guides and anchors attached to concrete.

END OF SECTION 220516